Centrefit Group

Electrician Install Procedure

Alarm Panel · Server Rack · Data · CCTV · Automation · Router · Nightlife

Step-by-step procedure for the electrician on a Centrefit fit-out. Work through the sections in order. Photo placeholders show what a finished install should look like — if your install doesn't match the photo, stop and check with the project manager before moving on.

# 1. Alarm Panel

## Mount and fit the alarm panel

Mount the alarm panel in the location shown on the plans.

Wire each cable into its correct labelled terminal — do not improvise terminations.

Confirm every cable is labelled correctly at both ends before powering on.

📷 Insert photo: Mounted alarm panel with all cables labelled and terminated

## Coax termination in the roof space

Terminate and split the coax in the roof space.

Run cables from the splitters down to the integration wall plate, alongside the antenna cable.

⚠ ONE feed cable per ONE splitter. Do not daisy-chain feeds across splitters.

📷 Insert photo: Roof-space splitters with feed cables labelled and running to integration wall plate

# 2. Server Rack

Pull the rack off the wall by approximately 1.5 metres — enough clearance to service behind it.

Mount the faceplates to the wall in their labelled positions.

If the site has more than 16 cameras, move the additional cameras (cam 17 onwards) onto the data wall plate.

Move the alarm panel data integration onto the data wall plate. See page 5 of the plans for the integration cable run.

Run all data cables into the patch panel.

📷 Insert photo: Server rack pulled off wall, faceplates mounted, data cabling tidied to patch panel

# 3. Data — Patch Panel Layout

Patch the following devices to the listed ports. Mis-patching here breaks the whole site.

| Patch Panel | Port | Device |
| --- | --- | --- |
| Patch 1 | Port 1 | NBN |
| Patch 1 | Port 2 | Alarm panel |
| Patch 1 | Port 3 | NVR |
| Patch 1 | Port 4 | Felixgate camera |
| Patch 1 | Port 5 | Felixgate sensor |
| Patch 1 | Port 6 onwards | WAPs (Wi-Fi access points) — one per port |
| Patch 2 | Port 1 onwards | Cameras 17+ (overflow when site has > 16 cameras) |

📷 Insert photo: Patch panel fully terminated with port labels visible

# 4. CCTV

Wire cameras 1 through 16 directly into the NVR.

Confirm each camera channel matches the labelled camera location.

📷 Insert photo: NVR rear with cameras 1–16 connected and labelled

# 5. Automation

## Antenna & coax

Wire the antenna into the splitter at the labelled port.

Wire the feed cables into the 8-port active tap.

📷 Insert photo: Splitter and 8-port active tap with antenna + feeds terminated and labelled

## Power supplies

⚠ Polarity matters. If the alarm panel or access control power supply is wired the wrong way around, you WILL blow up the controller. Double-check labels before powering on.

Wire in the alarm panel power supply — verify the labelled polarity is correct.

Wire in the access control power supply — verify the labelled polarity is correct.

Plug both power supplies into the powerboard that is plugged into the UPS at the bottom of the rack — not directly into the wall.

📷 Insert photo: Powerboard inside the UPS with alarm panel + access control supplies plugged in

## Audio

Wire the speaker cable into the amplifier.

If a second 120W amplifier is fitted, wire the second zone into its 100V speaker output.

WiiM (if fitted): If a WiiM player is fitted, unbox it and wire the supplied RCA plugs into Line 3 of the 120W amplifier — the cables will be labelled.

📷 Insert photo: Amplifier with speaker zones + WiiM RCA inputs wired and labelled

# 6. Router

Install the UniFi router on the top shelf of the rack.

📷 Insert photo: UniFi router mounted on the top shelf of the rack

# 7. Nightlife

Install the powerboard from the Nightlife kit and plug it into the battery / power-surge GPO of the UPS.

Install the Nightlife router on the top shelf of the rack.

Run the Nightlife kiosk from the data wall plate into the port labelled 'Nightlife Only' on the router.

Plug the client network into the patch panel, then through to the switch.

Plug the Nightlife server into its dedicated port on the Nightlife router.

📷 Insert photo: Nightlife router top shelf with kiosk, client network, and server cabled

# 8. Test Commission

Final walk-through with the project manager. Confirm every system is up before leaving site.

Alarm panel: power LED green, panel reports armed/disarmed correctly.

Server rack: all data link lights up, no orphaned cables.

CCTV: cameras 1–16 visible on NVR, cam 17+ (if any) reachable from the network.

Automation: amplifier zones audible, WiiM (if fitted) streaming to Line 3.

Router: UniFi reachable on management VLAN.

Nightlife: kiosk live, client network reachable, Nightlife server up.

All labels legible and final photos taken for the site Key Info tab.

📷 Insert photo: Final rack photo — door closed, labels visible, everything powered up

# Sign-off

| Site |  |
| --- | --- |
| Electrician |  |
| Centrefit project manager |  |
| Date |  |

Notes / Variances:

______________________________________________________________________________________________________________

______________________________________________________________________________________________________________

______________________________________________________________________________________________________________

______________________________________________________________________________________________________________

______________________________________________________________________________________________________________

______________________________________________________________________________________________________________